## Floor 1 points
Point List
Location: | One Hundred Gold Street / Floor 1 | Run Date: 1/10/2018 12:29:05 PM
Location | Control Program | Name | Type | Object ID | Device ID | Object Name | Offset / Polarity | Exp:Num | I/O Type
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Filter DP | BAI | AI:1 | DEV:241101 | filter_dp_1 | 0 | 0:02 | 0-20 mA
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Mixed Air Temp | BAI | AI:2 | DEV:241101 | mat_1 | 0 | 0:03 | Thermistor
/One Hundred Gold Street/Floor 1 | B1 NW Interior | RA Temperature | BAI | AI:3 | DEV:241101 | ra_temperature_1 | 0 | 0:01 | Thermistor
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Static Pressure | BAI | AI:4 | DEV:241101 | stat_press_1 | 0 | 0:07 | 0-20 mA
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Supply Air Temp. | BAI | AI:5 | DEV:241101 | sat_1 | 0 | 0:06 | Thermistor
/One Hundred Gold Street/Floor 1 | B1 NW Interior | SF Status | BBI | BI:1 | DEV:241101 | sf_status_1 | normal | 0:04 | Dry Contact
/One Hundred Gold Street/Floor 1 | B1 NW Interior | SF VFD Fault | BBI | BI:2 | DEV:241101 | sf_vfd_flt_1 | reversed | 0:05 | Dry Contact
/One Hundred Gold Street/Floor 1 | B1 NW Interior | CHW VLV | BAO | AO:1 | DEV:241101 | chw_vlv_1 | 0 | 0:01 | Electrical 0-10 Volt
/One Hundred Gold Street/Floor 1 | B1 NW Interior | SF VFD Speed | BAO | AO:2 | DEV:241101 | sf_vfd_output_1 | 0 | 0:03 | Electrical 0-10 Volt
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Stm Vlv | BAO | AO:3 | DEV:241101 | stm_vlv_1 | 0 | 0:02 | Electrical 0-10 Volt
/One Hundred Gold Street/Floor 1 | B1 NW Interior | SF S/S | BBO | BO:1 | DEV:241101 | sf_1 | normal | 0:01 | Relay / Triac Output
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Active Zone | BAV | AV:23 | DEV:241101 | active_zones_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Cooling Run Request | BAV | AV:1 | DEV:241101 | cl_run_for_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Cool Request | BAV | AV:2 | DEV:241101 | cool_request_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | EI Weighting | BAV | AV:24 | DEV:241101 | ei_weight_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Environmental Index Count | BAV | AV:25 | DEV:241101 | item_count_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Heating Run Request | BAV | AV:3 | DEV:241101 | ht_run_for_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Heat Request | BAV | AV:4 | DEV:241101 | heat_request_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Metric | BAV | AV:26 | DEV:241101 | metric_conv_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Output Override | BAV | AV:5 | DEV:241101 | clg_ovrde_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Output Override | BAV | AV:6 | DEV:241101 | htg_ovrde_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Output Override SFI | BAV | AV:22 | DEV:241101 | sat_ovrde_sfi_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | SA Static Pressure | BAV | AV:7 | DEV:241101 | dstpr_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | SF VFD Freq | BAV | AV:8 | DEV:241101 | sf_vfd_freq_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | SF VFD SPD OCC | BAV | AV:9 | DEV:241101 | sf_vfd_spd_occ_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | SF VFD SPD UNOCC | BAV | AV:10 | DEV:241101 | sf_vfd_spd_unocc_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Summer Setpt | BAV | AV:11 | DEV:241101 | summer_setpt_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Supply Air Temp Setpoint | BAV | AV:12 | DEV:241101 | sa_setpt_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Unocc CLG SA Setpt | BAV | AV:13 | DEV:241101 | unoc_clg_sa_spt_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Unocc HTG SA Setpt | BAV | AV:14 | DEV:241101 | unoc_htg_sa_spt_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Winter Setpt | BAV | AV:15 | DEV:241101 | winter_setpt_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Zone EI Time Satisfied | BAV | AV:27 | DEV:241101 | zn_ei_time_sat_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Zone EI Total Weight | BAV | AV:28 | DEV:241101 | total_weight_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Zone Environmental Index | BAV | AV:29 | DEV:241101 | zn_enviro_indx_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Zone Weighted Environmental Index | BAV | AV:30 | DEV:241101 | enviro_windx_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | AHU Clg Err | BBV | BV:21 | DEV:241101 | ahu_clg_err_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | AHU Htg Err | BBV | BV:22 | DEV:241101 | ahu_htg_err_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Boiler Status | BBV | BV:23 | DEV:241101 | boiler_status_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Filter Status | BBV | BV:1 | DEV:241101 | filter_status_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Manual Override Lock | BBV | BV:2 | DEV:241101 | man_ovrde_lock_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Manual Override State | BBV | BV:3 | DEV:241101 | man_ovrde_state_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Mode Type | BBV | BV:19 | DEV:241101 | weather_mode_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Output Override Lock | BBV | BV:4 | DEV:241101 | clg_ovrde_lock_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Output Override Lock | BBV | BV:5 | DEV:241101 | htg_ovrde_lock_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Output Override Lock SFI | BBV | BV:20 | DEV:241101 | sat_ovrde_lock_sfi_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Run | BBV | BV:6 | DEV:241101 | run_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Schedule | BBV | BV:7 | DEV:241101 | schedule_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Continuous Running Days | BMSV | MSV:1 | DEV:241101 | nonstop_days_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Cool Stuck Days | BMSV | MSV:2 | DEV:241101 | clstuck_days_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | CSATHI Days | BMSV | MSV:3 | DEV:241101 | csathi_days_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Heat Stuck Days | BMSV | MSV:4 | DEV:241101 | htstuck_days_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | High RAT Days | BMSV | MSV:5 | DEV:241101 | rathi_days_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | HSATLO Days | BMSV | MSV:6 | DEV:241101 | hsatlo_days_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | HtCl Days | BMSV | MSV:7 | DEV:241101 | htcl_days_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Low RAT Days | BMSV | MSV:8 | DEV:241101 | ratlo_days_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | CL_FAIL | BALM | BV:24 | DEV:241101 | cl_fail_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | CL_LEAK | BALM | BV:25 | DEV:241101 | cl_leak_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | CL_VLV_CYC | BALM | BV:26 | DEV:241101 | cl_vlv_cyc_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | CSAT_HI | BALM | BV:27 | DEV:241101 | csat_hi_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | FILTER | BALM | BV:8 | DEV:241101 | filter_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | HSAT_LO | BALM | BV:28 | DEV:241101 | hsat_lo_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | HT_FAIL | BALM | BV:29 | DEV:241101 | ht_fail_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | HT_STUCK | BALM | BV:30 | DEV:241101 | ht_stuck_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | HT_VLV_CYC | BALM | BV:31 | DEV:241101 | ht_vlv_cyc_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | HT/CL | BALM | BV:32 | DEV:241101 | htcl_sim_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | MAT_FAIL | BALM | BV:33 | DEV:241101 | mat_fail_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | MAT_HI | BALM | BV:9 | DEV:241101 | mat_hi_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | MAT_LO | BALM | BV:10 | DEV:241101 | mat_lo_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | NONSTOP | BALM | BV:34 | DEV:241101 | nonstop_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | RAT_FAIL | BALM | BV:35 | DEV:241101 | rat_fail_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | RAT_HI | BALM | BV:11 | DEV:241101 | rat_hi_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | RAT_LO | BALM | BV:12 | DEV:241101 | rat_lo_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | SAT_FAIL | BALM | BV:36 | DEV:241101 | sat_fail_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | SAT_HI | BALM | BV:13 | DEV:241101 | sat_hi_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | SAT_LO | BALM | BV:14 | DEV:241101 | sat_lo_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | SAT_OSTPT | BALM | BV:15 | DEV:241101 | sat_ostpt_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | SF_FAIL | BALM | BV:16 | DEV:241101 | sf_fail_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | SF_HAND | BALM | BV:17 | DEV:241101 | sf_hand_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | SFD_FLT | BALM | BV:18 | DEV:241101 | sfd_flt_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Boiler Status | BNI2 |  | DEV:241101
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Chiller Status | BNI2 |  | DEV:241101
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Mode Type | BNI |  | DEV:241101
/One Hundred Gold Street/Floor 1 | B1 NW Interior | OA Hum | ANI |  | DEV:241101
/One Hundred Gold Street/Floor 1 | B1 NW Interior | OA Temp | ANI |  | DEV:241101
/One Hundred Gold Street/Floor 1 | B1 NW Interior | SAT1 SFP | ANI |  | DEV:241101
/One Hundred Gold Street/Floor 1 | B1 NW Interior | SAT2 SFP | ANI |  | DEV:241101
/One Hundred Gold Street/Floor 1 | B1 NW Interior | Weather Mode | ANI |  | DEV:241101
/One Hundred Gold Street/Floor 1 | B1 NW Interior | CLG PID | BPID | LOOP:1 | DEV:241101 | clg_pid_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | CLG PID / Setpoint | BAV | AV:16 | DEV:241101 | clg_pid_setpt_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | CLG PID / Input | BAV | AV:17 | DEV:241101 | clg_pid_input_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | CLG PID / PID out | BAV | AV:18 | DEV:241101 | clg_pid_pidout_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | H PID | BPID | LOOP:2 | DEV:241101 | h_pid_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | H PID / Setpoint | BAV | AV:19 | DEV:241101 | h_pid_setpt_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | H PID / Input | BAV | AV:20 | DEV:241101 | h_pid_input_1
/One Hundred Gold Street/Floor 1 | B1 NW Interior | H PID / PID out | BAV | AV:21 | DEV:241101 | h_pid_pidout_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | CW Delta Pressure | BAI | AI:6 | DEV:240101 | delta_press_1 | 0 | 0:08 | 0-20 mA
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Filter DP | BAI | AI:1 | DEV:240101 | filter_dp_1 | 0 | 0:02 | 0-20 mA
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Mixed Air Temp | BAI | AI:2 | DEV:240101 | mat_1 | 0 | 0:03 | Thermistor
/One Hundred Gold Street/Floor 1 | B2 SW Interior | RA Temperature | BAI | AI:3 | DEV:240101 | ra_temperature_1 | 0 | 0:01 | Thermistor
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Static Pressure | BAI | AI:4 | DEV:240101 | stat_press_1 | 0 | 0:07 | 0-20 mA
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Supply Air Temp. | BAI | AI:5 | DEV:240101 | sat_1 | 0 | 0:06 | Thermistor
/One Hundred Gold Street/Floor 1 | B2 SW Interior | SF Status | BBI | BI:1 | DEV:240101 | sf_status_1 | normal | 0:04 | Dry Contact
/One Hundred Gold Street/Floor 1 | B2 SW Interior | SF VFD Fault | BBI | BI:2 | DEV:240101 | sf_vfd_flt_1 | reversed | 0:05 | Dry Contact
/One Hundred Gold Street/Floor 1 | B2 SW Interior | CHW VLV | BAO | AO:1 | DEV:240101 | chw_vlv_1 | 0 | 0:01 | Electrical 0-10 Volt
/One Hundred Gold Street/Floor 1 | B2 SW Interior | CW Byp Valve | BAO | AO:4 | DEV:240101 | cw_byp_vlv_output_1 | 0 | 0:04 | Electrical 0-10 Volt
/One Hundred Gold Street/Floor 1 | B2 SW Interior | SF VFD Speed | BAO | AO:2 | DEV:240101 | sf_vfd_output_1 | 0 | 0:03 | Electrical 0-10 Volt
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Stm Vlv | BAO | AO:3 | DEV:240101 | stm_vlv_1 | 0 | 0:02 | Electrical 0-10 Volt
/One Hundred Gold Street/Floor 1 | B2 SW Interior | SF S/S | BBO | BO:1 | DEV:240101 | sf_1 | normal | 0:01 | Relay / Triac Output
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Active Zone | BAV | AV:29 | DEV:240101 | active_zones_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Cooling Run Request | BAV | AV:1 | DEV:240101 | cl_run_for_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Cool Request | BAV | AV:2 | DEV:240101 | cool_request_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | CW Delta Pressure | BAV | AV:23 | DEV:240101 | cw_dp_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | CW DP Setpoint | BAV | AV:24 | DEV:240101 | cw_dp_stpt_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | EI Weighting | BAV | AV:30 | DEV:240101 | ei_weight_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Environmental Index Count | BAV | AV:31 | DEV:240101 | item_count_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Heating Run Request | BAV | AV:3 | DEV:240101 | ht_run_for_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Heat Request | BAV | AV:4 | DEV:240101 | heat_request_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Metric | BAV | AV:32 | DEV:240101 | metric_conv_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Output Override | BAV | AV:25 | DEV:240101 | bypvlv_ovrde_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Output Override | BAV | AV:5 | DEV:240101 | clg_ovrde_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Output Override | BAV | AV:6 | DEV:240101 | htg_ovrde_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Output Override SFI | BAV | AV:22 | DEV:240101 | sat_ovrde_sfi_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | SA Static Pressure | BAV | AV:7 | DEV:240101 | dstpr_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | SF VFD Freq | BAV | AV:8 | DEV:240101 | sf_vfd_freq_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | SF VFD SPD OCC | BAV | AV:9 | DEV:240101 | sf_vfd_spd_occ_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | SF VFD SPD UNOCC | BAV | AV:10 | DEV:240101 | sf_vfd_spd_unocc_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Summer Setpt | BAV | AV:11 | DEV:240101 | summer_setpt_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Supply Air Temp Setpoint | BAV | AV:12 | DEV:240101 | sa_setpt_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Unocc CLG SA Setpt | BAV | AV:13 | DEV:240101 | unoc_clg_sa_spt_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Unocc HTG SA Setpt | BAV | AV:14 | DEV:240101 | unoc_htg_sa_spt_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Winter Setpt | BAV | AV:15 | DEV:240101 | winter_setpt_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Zone EI Time Satisfied | BAV | AV:33 | DEV:240101 | zn_ei_time_sat_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Zone EI Total Weight | BAV | AV:34 | DEV:240101 | total_weight_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Zone Environmental Index | BAV | AV:35 | DEV:240101 | zn_enviro_indx_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Zone Weighted Environmental Index | BAV | AV:36 | DEV:240101 | enviro_windx_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Filter Status | BBV | BV:1 | DEV:240101 | filter_status_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Manual Override Lock | BBV | BV:2 | DEV:240101 | man_ovrde_lock_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Manual Override State | BBV | BV:3 | DEV:240101 | man_ovrde_state_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Mode Type | BBV | BV:19 | DEV:240101 | weather_mode_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Output Override Lock | BBV | BV:21 | DEV:240101 | bypvlv_ovrde_lock_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Output Override Lock | BBV | BV:4 | DEV:240101 | clg_ovrde_lock_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Output Override Lock | BBV | BV:5 | DEV:240101 | htg_ovrde_lock_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Output Override Lock SFI | BBV | BV:20 | DEV:240101 | sat_ovrde_lock_sfi_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Run | BBV | BV:6 | DEV:240101 | run_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Schedule | BBV | BV:7 | DEV:240101 | schedule_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | FILTER | BALM | BV:8 | DEV:240101 | filter_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | MAT_HI | BALM | BV:9 | DEV:240101 | mat_hi_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | MAT_LO | BALM | BV:10 | DEV:240101 | mat_lo_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | RAT_HI | BALM | BV:11 | DEV:240101 | rat_hi_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | RAT_LO | BALM | BV:12 | DEV:240101 | rat_lo_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | SAT_HI | BALM | BV:13 | DEV:240101 | sat_hi_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | SAT_LO | BALM | BV:14 | DEV:240101 | sat_lo_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | SAT_OSTPT | BALM | BV:15 | DEV:240101 | sat_ostpt_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | SF_FAIL | BALM | BV:16 | DEV:240101 | sf_fail_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | SF_HAND | BALM | BV:17 | DEV:240101 | sf_hand_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | SFD_FLT | BALM | BV:18 | DEV:240101 | sfd_flt_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Mode Type | BNI |  | DEV:240101
/One Hundred Gold Street/Floor 1 | B2 SW Interior | OA Hum | ANI |  | DEV:240101
/One Hundred Gold Street/Floor 1 | B2 SW Interior | OA Temp | ANI |  | DEV:240101
/One Hundred Gold Street/Floor 1 | B2 SW Interior | SAT1 SFP | ANI |  | DEV:240101
/One Hundred Gold Street/Floor 1 | B2 SW Interior | SAT2 SFP | ANI |  | DEV:240101
/One Hundred Gold Street/Floor 1 | B2 SW Interior | Weather Mode | ANI |  | DEV:240101
/One Hundred Gold Street/Floor 1 | B2 SW Interior | BACnet PID | BPID | LOOP:3 | DEV:240101 | m192_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | BACnet PID / Setpoint | BAV | AV:26 | DEV:240101 | m192_setpt_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | BACnet PID / Input | BAV | AV:27 | DEV:240101 | m192_input_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | BACnet PID / PID out | BAV | AV:28 | DEV:240101 | m192_pidout_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | CLG PID | BPID | LOOP:1 | DEV:240101 | clg_pid_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | CLG PID / Setpoint | BAV | AV:16 | DEV:240101 | clg_pid_setpt_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | CLG PID / Input | BAV | AV:17 | DEV:240101 | clg_pid_input_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | CLG PID / PID out | BAV | AV:18 | DEV:240101 | clg_pid_pidout_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | H PID | BPID | LOOP:2 | DEV:240101 | h_pid_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | H PID / Setpoint | BAV | AV:19 | DEV:240101 | h_pid_setpt_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | H PID / Input | BAV | AV:20 | DEV:240101 | h_pid_input_1
/One Hundred Gold Street/Floor 1 | B2 SW Interior | H PID / PID out | BAV | AV:21 | DEV:240101 | h_pid_pidout_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Filter DP | BAI | AI:1 | DEV:240102 | filter_dp_1 | 0 | 0:02 | 0-20 mA
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Mixed Air Temp | BAI | AI:2 | DEV:240102 | mat_1 | 0 | 0:03 | Thermistor
/One Hundred Gold Street/Floor 1 | B4 SE Interior | RA Temperature | BAI | AI:3 | DEV:240102 | ra_temperature_1 | 0 | 0:01 | Thermistor
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Static Pressure | BAI | AI:4 | DEV:240102 | stat_press_1 | 0 | 0:07 | 0-20 mA
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Supply Air Temp. | BAI | AI:5 | DEV:240102 | sat_1 | 0 | 0:06 | Thermistor
/One Hundred Gold Street/Floor 1 | B4 SE Interior | SF Status | BBI | BI:1 | DEV:240102 | sf_status_1 | normal | 0:04 | Dry Contact
/One Hundred Gold Street/Floor 1 | B4 SE Interior | SF VFD Fault | BBI | BI:2 | DEV:240102 | sf_vfd_flt_1 | reversed | 0:05 | Dry Contact
/One Hundred Gold Street/Floor 1 | B4 SE Interior | CHW VLV | BAO | AO:1 | DEV:240102 | chw_vlv_1 | 0 | 0:01 | Electrical 0-10 Volt
/One Hundred Gold Street/Floor 1 | B4 SE Interior | SF VFD Speed | BAO | AO:2 | DEV:240102 | sf_vfd_output_1 | 0 | 0:03 | Electrical 0-10 Volt
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Stm Vlv | BAO | AO:3 | DEV:240102 | stm_vlv_1 | 0 | 0:02 | Electrical 0-10 Volt
/One Hundred Gold Street/Floor 1 | B4 SE Interior | SF S/S | BBO | BO:1 | DEV:240102 | sf_1 | normal | 0:01 | Relay / Triac Output
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Active Zone | BAV | AV:23 | DEV:240102 | active_zones_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Cooling Run Request | BAV | AV:1 | DEV:240102 | cl_run_for_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Cool Request | BAV | AV:2 | DEV:240102 | cool_request_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | EI Weighting | BAV | AV:24 | DEV:240102 | ei_weight_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Environmental Index Count | BAV | AV:25 | DEV:240102 | item_count_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Heating Run Request | BAV | AV:3 | DEV:240102 | ht_run_for_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Heat Request | BAV | AV:4 | DEV:240102 | heat_request_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Metric | BAV | AV:26 | DEV:240102 | metric_conv_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Output Override | BAV | AV:5 | DEV:240102 | clg_ovrde_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Output Override | BAV | AV:6 | DEV:240102 | htg_ovrde_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Output Override SFI | BAV | AV:22 | DEV:240102 | sat_ovrde_sfi_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | SA Static Pressure | BAV | AV:7 | DEV:240102 | dstpr_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | SF VFD Freq | BAV | AV:8 | DEV:240102 | sf_vfd_freq_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | SF VFD SPD OCC | BAV | AV:9 | DEV:240102 | sf_vfd_spd_occ_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | SF VFD SPD UNOCC | BAV | AV:10 | DEV:240102 | sf_vfd_spd_unocc_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Summer Setpt | BAV | AV:11 | DEV:240102 | summer_setpt_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Supply Air Temp Setpoint | BAV | AV:12 | DEV:240102 | sa_setpt_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Unocc CLG SA Setpt | BAV | AV:13 | DEV:240102 | unoc_clg_sa_spt_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Unocc HTG SA Setpt | BAV | AV:14 | DEV:240102 | unoc_htg_sa_spt_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Winter Setpt | BAV | AV:15 | DEV:240102 | winter_setpt_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Zone EI Time Satisfied | BAV | AV:27 | DEV:240102 | zn_ei_time_sat_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Zone EI Total Weight | BAV | AV:28 | DEV:240102 | total_weight_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Zone Environmental Index | BAV | AV:29 | DEV:240102 | zn_enviro_indx_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Zone Weighted Environmental Index | BAV | AV:30 | DEV:240102 | enviro_windx_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | AHU Clg Err | BBV | BV:21 | DEV:240102 | ahu_clg_err_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | AHU Htg Err | BBV | BV:22 | DEV:240102 | ahu_htg_err_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Boiler Status | BBV | BV:23 | DEV:240102 | boiler_status_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Filter Status | BBV | BV:1 | DEV:240102 | filter_status_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Manual Override Lock | BBV | BV:2 | DEV:240102 | man_ovrde_lock_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Manual Override State | BBV | BV:3 | DEV:240102 | man_ovrde_state_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Mode Type | BBV | BV:19 | DEV:240102 | weather_mode_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Output Override Lock | BBV | BV:4 | DEV:240102 | clg_ovrde_lock_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Output Override Lock | BBV | BV:5 | DEV:240102 | htg_ovrde_lock_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Output Override Lock SFI | BBV | BV:20 | DEV:240102 | sat_ovrde_lock_sfi_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Run | BBV | BV:6 | DEV:240102 | run_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Schedule | BBV | BV:7 | DEV:240102 | schedule_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Continuous Running Days | BMSV | MSV:1 | DEV:240102 | nonstop_days_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Cool Stuck Days | BMSV | MSV:2 | DEV:240102 | clstuck_days_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | CSATHI Days | BMSV | MSV:3 | DEV:240102 | csathi_days_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Heat Stuck Days | BMSV | MSV:4 | DEV:240102 | htstuck_days_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | High RAT Days | BMSV | MSV:5 | DEV:240102 | rathi_days_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | HSATLO Days | BMSV | MSV:6 | DEV:240102 | hsatlo_days_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | HtCl Days | BMSV | MSV:7 | DEV:240102 | htcl_days_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Low RAT Days | BMSV | MSV:8 | DEV:240102 | ratlo_days_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | CL_FAIL | BALM | BV:24 | DEV:240102 | cl_fail_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | CL_LEAK | BALM | BV:25 | DEV:240102 | cl_leak_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | CL_VLV_CYC | BALM | BV:26 | DEV:240102 | cl_vlv_cyc_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | CSAT_HI | BALM | BV:27 | DEV:240102 | csat_hi_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | FILTER | BALM | BV:8 | DEV:240102 | filter_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | HSAT_LO | BALM | BV:28 | DEV:240102 | hsat_lo_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | HT_FAIL | BALM | BV:29 | DEV:240102 | ht_fail_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | HT_STUCK | BALM | BV:30 | DEV:240102 | ht_stuck_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | HT_VLV_CYC | BALM | BV:31 | DEV:240102 | ht_vlv_cyc_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | HT/CL | BALM | BV:32 | DEV:240102 | htcl_sim_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | MAT_FAIL | BALM | BV:33 | DEV:240102 | mat_fail_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | MAT_HI | BALM | BV:9 | DEV:240102 | mat_hi_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | MAT_LO | BALM | BV:10 | DEV:240102 | mat_lo_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | NONSTOP | BALM | BV:34 | DEV:240102 | nonstop_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | RAT_FAIL | BALM | BV:35 | DEV:240102 | rat_fail_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | RAT_HI | BALM | BV:11 | DEV:240102 | rat_hi_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | RAT_LO | BALM | BV:12 | DEV:240102 | rat_lo_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | SAT_FAIL | BALM | BV:36 | DEV:240102 | sat_fail_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | SAT_HI | BALM | BV:13 | DEV:240102 | sat_hi_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | SAT_LO | BALM | BV:14 | DEV:240102 | sat_lo_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | SAT_OSTPT | BALM | BV:15 | DEV:240102 | sat_ostpt_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | SF_FAIL | BALM | BV:16 | DEV:240102 | sf_fail_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | SF_HAND | BALM | BV:17 | DEV:240102 | sf_hand_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | SFD_FLT | BALM | BV:18 | DEV:240102 | sfd_flt_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Boiler Status | BNI2 |  | DEV:240102
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Chiller Status | BNI2 |  | DEV:240102
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Mode Type | BNI |  | DEV:240102
/One Hundred Gold Street/Floor 1 | B4 SE Interior | OA Hum | ANI |  | DEV:240102
/One Hundred Gold Street/Floor 1 | B4 SE Interior | OA Temp | ANI |  | DEV:240102
/One Hundred Gold Street/Floor 1 | B4 SE Interior | SAT1 SFP | ANI |  | DEV:240102
/One Hundred Gold Street/Floor 1 | B4 SE Interior | SAT2 SFP | ANI |  | DEV:240102
/One Hundred Gold Street/Floor 1 | B4 SE Interior | Weather Mode | ANI |  | DEV:240102
/One Hundred Gold Street/Floor 1 | B4 SE Interior | CLG PID | BPID | LOOP:1 | DEV:240102 | clg_pid_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | CLG PID / Setpoint | BAV | AV:16 | DEV:240102 | clg_pid_setpt_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | CLG PID / Input | BAV | AV:17 | DEV:240102 | clg_pid_input_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | CLG PID / PID out | BAV | AV:18 | DEV:240102 | clg_pid_pidout_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | H PID | BPID | LOOP:2 | DEV:240102 | h_pid_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | H PID / Setpoint | BAV | AV:19 | DEV:240102 | h_pid_setpt_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | H PID / Input | BAV | AV:20 | DEV:240102 | h_pid_input_1
/One Hundred Gold Street/Floor 1 | B4 SE Interior | H PID / PID out | BAV | AV:21 | DEV:240102 | h_pid_pidout_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Filter DP | BAI | AI:1 | DEV:240103 | filter_dp_1 | 0 | 0:02 | 0-20 mA
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Mixed Air Temp | BAI | AI:2 | DEV:240103 | mat_1 | 0 | 0:03 | Thermistor
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | RA Temperature | BAI | AI:3 | DEV:240103 | ra_temperature_1 | 0 | 0:01 | Thermistor
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Static Pressure | BAI | AI:4 | DEV:240103 | stat_press_1 | 0 | 0:07 | 0-20 mA
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Supply Air Temp. | BAI | AI:5 | DEV:240103 | sat_1 | 0 | 0:06 | Thermistor
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | SF Status | BBI | BI:1 | DEV:240103 | sf_status_1 | normal | 0:04 | Dry Contact
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | SF VFD Fault | BBI | BI:2 | DEV:240103 | sf_vfd_flt_1 | reversed | 0:05 | Dry Contact
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | CHW VLV | BAO | AO:1 | DEV:240103 | chw_vlv_1 | 0 | 0:01 | Electrical 0-10 Volt
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | SF VFD Speed | BAO | AO:2 | DEV:240103 | sf_vfd_output_1 | 0 | 0:03 | Electrical 0-10 Volt
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Stm Vlv | BAO | AO:3 | DEV:240103 | stm_vlv_1 | 0 | 0:02 | Electrical 0-10 Volt
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | SF S/S | BBO | BO:1 | DEV:240103 | sf_1 | normal | 0:01 | Relay / Triac Output
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Active Zone | BAV | AV:23 | DEV:240103 | active_zones_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Cooling Run Request | BAV | AV:1 | DEV:240103 | cl_run_for_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Cool Request | BAV | AV:2 | DEV:240103 | cool_request_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | EI Weighting | BAV | AV:24 | DEV:240103 | ei_weight_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Environmental Index Count | BAV | AV:25 | DEV:240103 | item_count_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Heating Run Request | BAV | AV:3 | DEV:240103 | ht_run_for_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Heat Request | BAV | AV:4 | DEV:240103 | heat_request_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Metric | BAV | AV:26 | DEV:240103 | metric_conv_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Output Override | BAV | AV:5 | DEV:240103 | clg_ovrde_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Output Override | BAV | AV:6 | DEV:240103 | htg_ovrde_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Output Override SFI | BAV | AV:22 | DEV:240103 | sat_ovrde_sfi_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | SA Static Pressure | BAV | AV:7 | DEV:240103 | dstpr_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | SF VFD Freq | BAV | AV:8 | DEV:240103 | sf_vfd_freq_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | SF VFD SPD OCC | BAV | AV:9 | DEV:240103 | sf_vfd_spd_occ_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | SF VFD SPD UNOCC | BAV | AV:10 | DEV:240103 | sf_vfd_spd_unocc_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Summer Setpt | BAV | AV:11 | DEV:240103 | summer_setpt_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Supply Air Temp Setpoint | BAV | AV:12 | DEV:240103 | sa_setpt_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Unocc CLG SA Setpt | BAV | AV:13 | DEV:240103 | unoc_clg_sa_spt_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Unocc HTG SA Setpt | BAV | AV:14 | DEV:240103 | unoc_htg_sa_spt_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Winter Setpt | BAV | AV:15 | DEV:240103 | winter_setpt_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Zone EI Time Satisfied | BAV | AV:27 | DEV:240103 | zn_ei_time_sat_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Zone EI Total Weight | BAV | AV:28 | DEV:240103 | total_weight_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Zone Environmental Index | BAV | AV:29 | DEV:240103 | zn_enviro_indx_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Zone Weighted Environmental Index | BAV | AV:30 | DEV:240103 | enviro_windx_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | AHU Clg Err | BBV | BV:21 | DEV:240103 | ahu_clg_err_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | AHU Htg Err | BBV | BV:22 | DEV:240103 | ahu_htg_err_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Boiler Status | BBV | BV:23 | DEV:240103 | boiler_status_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Filter Status | BBV | BV:1 | DEV:240103 | filter_status_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Manual Override Lock | BBV | BV:2 | DEV:240103 | man_ovrde_lock_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Manual Override State | BBV | BV:3 | DEV:240103 | man_ovrde_state_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Mode Type | BBV | BV:19 | DEV:240103 | weather_mode_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Output Override Lock | BBV | BV:4 | DEV:240103 | clg_ovrde_lock_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Output Override Lock | BBV | BV:5 | DEV:240103 | htg_ovrde_lock_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Output Override Lock SFI | BBV | BV:20 | DEV:240103 | sat_ovrde_lock_sfi_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Run | BBV | BV:6 | DEV:240103 | run_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Schedule | BBV | BV:7 | DEV:240103 | schedule_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Continuous Running Days | BMSV | MSV:1 | DEV:240103 | nonstop_days_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Cool Stuck Days | BMSV | MSV:2 | DEV:240103 | clstuck_days_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | CSATHI Days | BMSV | MSV:3 | DEV:240103 | csathi_days_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Heat Stuck Days | BMSV | MSV:4 | DEV:240103 | htstuck_days_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | High RAT Days | BMSV | MSV:5 | DEV:240103 | rathi_days_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | HSATLO Days | BMSV | MSV:6 | DEV:240103 | hsatlo_days_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | HtCl Days | BMSV | MSV:7 | DEV:240103 | htcl_days_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Low RAT Days | BMSV | MSV:8 | DEV:240103 | ratlo_days_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | CL_FAIL | BALM | BV:24 | DEV:240103 | cl_fail_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | CL_LEAK | BALM | BV:25 | DEV:240103 | cl_leak_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | CL_VLV_CYC | BALM | BV:26 | DEV:240103 | cl_vlv_cyc_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | CSAT_HI | BALM | BV:27 | DEV:240103 | csat_hi_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | FILTER | BALM | BV:8 | DEV:240103 | filter_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | HSAT_LO | BALM | BV:28 | DEV:240103 | hsat_lo_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | HT_FAIL | BALM | BV:29 | DEV:240103 | ht_fail_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | HT_STUCK | BALM | BV:30 | DEV:240103 | ht_stuck_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | HT_VLV_CYC | BALM | BV:31 | DEV:240103 | ht_vlv_cyc_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | HT/CL | BALM | BV:32 | DEV:240103 | htcl_sim_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | MAT_FAIL | BALM | BV:33 | DEV:240103 | mat_fail_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | MAT_HI | BALM | BV:9 | DEV:240103 | mat_hi_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | MAT_LO | BALM | BV:10 | DEV:240103 | mat_lo_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | NONSTOP | BALM | BV:34 | DEV:240103 | nonstop_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | RAT_FAIL | BALM | BV:35 | DEV:240103 | rat_fail_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | RAT_HI | BALM | BV:11 | DEV:240103 | rat_hi_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | RAT_LO | BALM | BV:12 | DEV:240103 | rat_lo_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | SAT_FAIL | BALM | BV:36 | DEV:240103 | sat_fail_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | SAT_HI | BALM | BV:13 | DEV:240103 | sat_hi_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | SAT_LO | BALM | BV:14 | DEV:240103 | sat_lo_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | SAT_OSTPT | BALM | BV:15 | DEV:240103 | sat_ostpt_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | SF_FAIL | BALM | BV:16 | DEV:240103 | sf_fail_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | SF_HAND | BALM | BV:17 | DEV:240103 | sf_hand_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | SFD_FLT | BALM | BV:18 | DEV:240103 | sfd_flt_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Boiler Status | BNI2 |  | DEV:240103
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Chiller Status | BNI2 |  | DEV:240103
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Mode Type | BNI |  | DEV:240103
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | OA Hum | ANI |  | DEV:240103
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | OA Temp | ANI |  | DEV:240103
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | SAT1 SFP | ANI |  | DEV:240103
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | SAT2 SFP | ANI |  | DEV:240103
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | Weather Mode | ANI |  | DEV:240103
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | CLG PID | BPID | LOOP:1 | DEV:240103 | clg_pid_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | CLG PID / Setpoint | BAV | AV:16 | DEV:240103 | clg_pid_setpt_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | CLG PID / Input | BAV | AV:17 | DEV:240103 | clg_pid_input_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | CLG PID / PID out | BAV | AV:18 | DEV:240103 | clg_pid_pidout_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | H PID | BPID | LOOP:2 | DEV:240103 | h_pid_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | H PID / Setpoint | BAV | AV:19 | DEV:240103 | h_pid_setpt_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | H PID / Input | BAV | AV:20 | DEV:240103 | h_pid_input_1
/One Hundred Gold Street/Floor 1 | B3 NE Interior (no steam) | H PID / PID out | BAV | AV:21 | DEV:240103 | h_pid_pidout_1